## Water Balance Calculations
Area
Utilities | Cooling Tower
Cooling Tower Equations
Tower Makeup = Evaporation + Windage/drift+ Cooling Tower blow down
Makeup * Xm = Evaporation * 0+ Windage * Xb+ Blow down * Xb
Blow down = (Windage* (Xb/Xm-1)-Evaporation)/(1-Xb/Xm)
|  | Value | Units |  |  | Value | Units
|  | Present |  |  |  | After Water Treatment Upgrade |  | Water Reduction (gpd)
Windage
| Tower Recirculation | 9900 | gpm |  |  | 9900 | gpm
| Windage Rate | 0.1% | % |  |  | 0.1% | %
| Windage | 14256 | gpd |  |  | 14256 | gpd | 0
Evaporation
| Delta T | 8 | F |  |  | 8 | F
| Evaporation | 114048 | gpd |  |  | 114048 | gpd | 0
#
Blow down
| Cycles of Concentration | 4 | number |  |  | 8 | number
| Blowdown | 23760 | gpd |  |  | 2036.5714 | gpd
| Cooling Tower Makeup | 152064 | gpd |  |  | 130340.5714 | gpd
Boiler
| Steam Generation | 20000 | lbs/hour |  |  | 20000 | lbs/hour
| Boiler Makeup | 13300 | lbs/hour | 38273.3813 | gpd | 11000 | lbs/hour
| Returned Condensate | 10000 | lbs/hour |  |  | 10000 | lbs/hour
| Blowdown @ 4 cycles | 3325 | lbs/hour | 9568.3453 | gpd | 1000 | gpd
Cooling Tower & Boiler Inputs & Outputs
| Cooling Tower Makeup + Boiler Makeup | 190337.3813 | gpd |  |  | 161995.2477 | gpd
| Water Treatment Wastewaters | 9516.8691 | gpd |  |  | 1000 | gpd
| Total Inputs into Utilities | 199854.2504 | gpd |  |  | 162995.2477 | gpd | 36859.0027
| Evaporation | 157080.9784 | gpd |  |  | 157080.9784 | gpd
| Utilites Wastewater | 42845.2144 | gpd |  |  | 4036.5714 | gpd
Sanitary | 1200 people time 25 gallons/person/shift | 30000 | gpd |  |  | 30000 | gpd
Irrigation | Count number of heads per zone multiply by rated capacity multiply by sprinkling time. Sum the flows for all zones | 29000 | gpd |  |  | 29000 | gpd
| Estimated leaks based upon engineering judgment | 5000 | gpd |  |  | 0 | gpd
|  | 34000 | gpd |  |  | 29000 | gpd | 5000
| Water Reduction | [6 empty] | 36859.0027